## Check Total lights heating
thermal zone
Power (W/m2) | cond.Surface (m2) | Heat transfer (W) | Schedule coeff. | Heat Transfer (W) | Lights Total Heating Energy (J) | Lights Total Heating Energy (Wh)
1.5 | 44 | 66 | 0.3 | 19.8 | 71261 | 19.7947
2 | 28.56 | 57.12
2 | 74.25 | 148.5
2 | 64.57 | 129.14
1.5 | 28.56 | 42.84
1.5 | 34.89 | 52.335
1 | 46.64 | 46.64
1.5 | 126.43 | 189.645
2 | 74.25 | 148.5
|  | 880.72 | W

## Heatbalance
[7 empty] | xe (kgawater/kgdryair) | Site Outdoor Air Humidity Ratio
Thermal zone | Masterbed | Conditioned area (m2) | 100 | Height (m) | 3 |  | xi (kgawater/kgdryair) | Zone Air Humidity Ratio | [16 empty] | Natural ventilation and infiltration gain/Loss
date | Outdoor Dbt (°C) | Indoor Dbt (°C) | ΔT (°K) | xe (kgawater/kgdryair) | xi (kgawater/kgdryair) | xe-xi (kgwater/kgdryair) | ΔT >0 | Heat loss | [6 empty] | GuideF conventional Surface Thermal Resistance (Convection+radiation) | [10 empty] | EPDRM Outdoor DBT (°C) | Setpoint (°C) | ΔT (°C) | h per month | Hve (W/K) | Qve (kW) | Qve(kWh) | then
01/01 05:00:00 | 14.83 | 17.49 | 2.66 | 0.0070393 | 0.0072287 | -0.00018943 | ΔT <0 | Heat gain | [6 empty] | [m2K/W] | Upwards (Roofs) | Horizontal (exp. Walls) | Downwards (exp floors) | [6 empty] | Jan | 12.2 | 19 | 6.8 | 744 | 437.71 | 2.9764 | 2214.4624 | Qh/Qc= ΣQtr+Qve
[15 empty] | Rsi | 0.14 | 0.1 | 0.14 | [6 empty] | Feb | 12.4 | 19 | 6.6 | 672 | 437.71 | 2.8889 | 1941.3314
| Surface thermal resistance in U value not included because is calculated by Eplus | [13 empty] | Rse | 0.04 | 0.06 | 0.04 | [6 empty] | Mar | 13.4 | 19 | 5.6 | 744 | 437.71 | 2.4512 | 1823.6749
Convection and conduction | Exposure | Opaque Area (m2) | U value (W/m2K) | SubTotal wall Conduction Heat Transfer (W/K) | Glazing Area (m2) | U value (W/m2K) | SubTotalGlazing Transfer (W/K) | Total Conduction Heat Transfer (W/K) | Total Conduction Heat Transfer (W) | [15 empty] | Apr | 15.5 | 19 | 3.5 | 720 | 437.71 | 1.532 | 1103.0292
| west | 28 | 0.83 | 23.24 | 1.272 | 2.8 | 3.5616 | 104.4902 | 277.9439 |  | 17.6064 | 46.833 |  |  | GuideF conventional Surface Thermal Transmittance (Convection+radiation) | [9 empty] | May | 19.1 | 26.5 | 7.4 | 744 | 437.71 | 3.2391 | 2409.8562
| NW | 18.69 | 1.36 | 25.4184 | 1.656 | 2.8 | 4.6368 | [7 empty] | [W/m2K] | Upwards (Roofs) | Horizontal (exp. Walls) | Downwards (exp floors) | [6 empty] | Jun | 23 | 26.5 | 3.5 | 720 | 437.71 | 1.532 | 1103.0292
| SE | 10.06 | 1.34 | 13.4804 |  |  | 0 | [7 empty] | Usi | 7.1429 | 10 | 7.1429 | [6 empty] | Jul | 25.9 | 26.5 | 0.6 | 744 | 437.71 | 0.26263 | 195.3937
| S | 25.25 | 0.98 | 24.745 | 3.36 | 2.8 | 9.408 | [7 empty] | Use | 25 | 16.6667 | 25 | [6 empty] | Aug | 26.3 | 26.5 | 0.2 | 744 | 437.71 | 0.087542 | 65.1312
[25 empty] | Sep | 24.1 | 26.5 | 2.4 | 720 | 437.71 | 1.0505 | 756.3629
| ACH -sensible | Volume (m3) | air Density * specific Heat (Wh/m3 K) | Infiltration (m) | ACH inf | Eplus Schedule Coefficient | Convection Heat Transfer Sensible(Wh) | [17 empty] | Oct | 20.7 | 26.5 | 5.8 | 744 | 437.71 | 2.5387 | 1888.8062
| 0.9 | 300 | 0.33333 |  |  | 1 | 239.4 | [7 empty] | From EPDRM Notes | [9 empty] | Nov | 17 | 19 | 2 | 720 | 437.71 | 0.87542 | 630.3024
| ACH -latent | Volume (m3) | r calore latente di vaporizzazione dell’acqua (Wh/ Kg) | densita dellária (kg/m3) | Infiltration (m) | ACH inf | Eplus Schedule Coefficient | Convection Heat Transfer Latent (Wh) | [6 empty] | Month | Isol_Daily global solar irradiation, W/m2 | [8 empty] | Dec | 13.8 | 19 | 5.2 | 744 | 437.71 | 2.2761 | 1693.4124
| 0.9 | 300 | 694.7222 | 1.2 |  |  | 1 | -42.6395 | [7 empty] | HOR | VERTICAL
[17 empty] | N | NE | E | SE | S | SW | W | NW
[15 empty] | Jan | 109.5833 | 28.75 | 30.4167 | 66.6667 | 125.8333 | 170 | 136.6667 | 75.8333 | 32.5
[15 empty] | Feb | 149.5833 | 40 | 47.9167 | 95 | 150 | 182.0833 | 144.5833 | 90 | 46.25
Internal Gain and solar gains | Exposure | Solar beam (W/m2) | Shading Factor | Opaque Area (m2) | Ext Adsorptance | U value (W/m2K) | Thermal Transmittance of ext surface (W/m2K) | Conductive Solar Heat Gain (W) | Total Conductive Solar Heat Gain (W) | [5 empty] | Mar | 208.3333 | 49.5833 | 71.25 | 126.25 | 165 | 180.4167 | 164.5833 | 127.5 | 73.75
| H | 0 | 0.59 | 42.72 | 0.9 | 0.49 | 25 | 0 | 0 | [5 empty] | Apr | 247.9167 | 59.5833 | 99.1667 | 146.6667 | 155.8333 | 137.9167 | 149.1667 | 139.1667 | 95.4167 | [8 empty] | and internal gains
| NW | 0 | 1 | 18.69 | 0.5 | 1.25 | 16.66 | 0 | [6 empty] | May | 305.8333 | 77.9167 | 130.4167 | 172.5 | 159.1667 | 119.1667 | 159.1667 | 171.25 | 129.1667
| SE | 0 | 0.8 | 10.06 | 0.5 | 1.19 | 16.66 | 0 | [6 empty] | Jun | 324.5833 | 95 | 150.4167 | 185.8333 | 155.8333 | 102.5 | 154.1667 | 183.75 | 148.75
| S | 0 | 1 | 25.25 | 0.5 | 0.87 | 16.66 | 0 | [6 empty] | Jul | 330 | 85 | 139.5833 | 180.4167 | 158.75 | 110 | 162.5 | 187.9167 | 146.25
[15 empty] | Aug | 290.4167 | 65 | 114.5833 | 165 | 166.6667 | 139.1667 | 165 | 162.0833 | 112.5
| Exposure | Solar beam (W/m2) | Shading Factor | Glazing Area (m2) | g value | Direct Solar Heat Gain (W) | Room Adsorptance | Total Direct Solar Heat Gain (W) | [6 empty] | Sep | 234.1667 | 54.1667 | 89.5833 | 147.9167 | 175.4167 | 172.9167 | 164.1667 | 135 | 82.5
| H | 0 | 1 | 1.272 | 0.52 | 0 | 0.8 | 0 | [6 empty] | Oct | 170.8333 | 42.5 | 52.5 | 100.8333 | 151.25 | 186.25 | 160 | 109.1667 | 55.8333
| NW | 0 | 0.82 | 1.656 | 0.52 | 0 | [8 empty] | Nov | 127.0833 | 33.3333 | 38.75 | 86.6667 | 150.8333 | 185.8333 | 139.5833 | 77.5 | 36.25
| SE | 0 | 0.79 | 3.36 | 0.52 | 0 | [8 empty] | Dec | 96.6667 | 28.3333 | 29.1667 | 60 | 115.8333 | 149.5833 | 113.75 | 58.75 | 29.1667
0
| People Heat Gain (W/m2) | Eplus schedule coefficient | Light Heat Gain (W/m2) | Eplus schedule coefficient | Appliances Heat Gain (W/m2) | Eplus schedule coefficient | Total H G (W)
| 1.5 | 0.3 | 1.5 | 0.3 | 1.2 | 0.3 | 126
Thermal Mass (int.side) | Exposure and Int.Material | Density (kg/m3) | Specific Heat Capacity (Wh/kgK) | Surface Area (m2) | Effective thickness (m) | DHC (Wh/K) | hourly Avg (Wh/K) | hourly Avg (Wh) | Total DHC (Wh) | Hourly avg (wH)
| W (glob) | 2000 | 0.27778 | 28 | 0.1 | 1555.5556 | 64.8148 | 172.4074 | 7428.4583 | 309.5191
|  | 1200 | 0.23333 | 18.69 | 0.1 | 523.32 | 21.805 | 58.0013
|  | 33 | 0.40833 | 10.06 | 0.05 | 6.7779 | 0.28241 | 0.75122 | [8 empty] | VERTICAL N: Juan Valleyo Balance
|  | 1200 | 0.23333 | 25.25 | 0.1 | 707 | 29.4583 | 78.3592
Results of Manual Calculations
Zone Sensible Heat Needs per hour
| Conduction Heat Transfer (W) | Convection Heat Transfer (W) | Solar Direct Heat Gain (W) | Solar Conductive HG (W) | Internal HG (W) | Thermal Mass (W)
| 277.9439 | 239.4 | 0 | 0 | 126 | 309.5191
Tot Sensible Heat/Cooling Needs (kW)
0.95286
Energy plus results
Zone Air heat balance (lat+sens) | Zone Air Heat Balance Surface Convection Rate (W) | Zone Air Heat Balance Internal Convective Heat Gain Rate (W) | Zone Air Heat Balance Interzone Air Transfer Rate (W) | Zone Air Heat Balance Outdoor Air Transfer Rate (W) | Zone Air Heat Balance System Air Transfer Rate (W) | The Zone Air Heat Balance System Convective Heat Gain Rate (W) | Sum (W) | Zone Air Heat Balance Air Energy Storage Rate [W]
0
[7 empty] | Sum = Zone AHB Energy storage |  |  |  | Surface Inside Face Convection Heat Transfer Coefficient
Heat balance per opaque surface | Surface Average Face Conduction Heat Transfer Rate | Surface Outside Face Convection Heat Transfer Coefficient | Opaque area | Surface Outside Face Incident Solar Radiation Rate per Area | adsorption coef. Of ext wall | Site Outdoor Air Drybulb Temperature | Air sol Temperature | Conduction through walls | Glazing Area (m2) | Glass U value (W/m2K) |  |  | Surface Inside Face Temperature | Surface Heat Storage Rate
| -499 | [12 empty] | -1262
| Zone Ideal Loads Zone Sensible Cooling Energy (J) | Zone Ideal Loads Zone Sensible heating Energy (J) | Zone Air Temperature (°C) | Zone Windows Total Heat Gain Energy (J) | Zone Windows Total Heat Loss Energy (J) | Lights Total Heating Energy (J) | Zone Electric Equipment Total Heating Energy (J) | Surface Heat Storage Energy (J)
Overall zone results (sensible) | 0 | 0 | 17.49 | 0 | -300675 | 71261.45 | 128270.5967
| (W) | ( W) |  | (W) | ( W) | (W) | ( W) | ( W)
| 0 | 0 |  | 0 | -83.5208 | 19.7948 | 35.6307 | 0
Sotto l'ipotesi di zone termiche disaccoppiate termicamente, escludendo contributo della massa termica interna e flussi di massa (aira interna tra le zone).(rapp tec 2014 pag 14) Nell’equazione di equilibrio energetico dell’aria, sopra scritta, si ha a primo membro l’accumulo termico nell’aria e a secondo membro, in ordine, si hanno gli scambi termici per trasmissione con le pareti7, il calore di ventilazione, il calore per sorgenti interne e per sorgenti ausiliarie (positivo se per riscaldamento e negativo per raffrescamento) ed infine il flusso attraverso le porte e le finestre. (Si assume che nel tempo infinitesimo dt ci sia equilibrio termico)
Note on D13: Luca Caruso: consider just one hour
Note on F14: Luca Caruso: check
Note on D15: Luca Caruso: consider just one hour
Note on I15: Luca Caruso: Equazione della ventilazione col latente dal metodo carrier (cammarata IT 2014 - Condizionamento pag 46
Note on G16: Luca Caruso: check
Note on C20: Luca Caruso: from the EPDRM notes
Note on D20: Luca Caruso: from datalist epdrm
Note on H20: Luca Caruso: from surface resistance guide f
Note on C26: Luca Caruso: from the EPDRM notes
Note on D26: Luca Caruso: from datalist epdrm
Note on D35: Luca Caruso: Cibse Guide A-consider just one hour
Note on G35: Luca Caruso: Diurnal heat capacity
Note on B56: Luca Caruso: scambi convettivi con le superfici interne
Note on C56: Luca Caruso: Calore trasferito dagli internal gain all'aria
Note on D56: Luca Caruso: scambi di massa con le altre zone accoppiate
Note on E56: Luca Caruso: Calore dell'aria proveniente dall'esterno (nat ventilation and infiltration )
Note on F56: Luca Caruso: calore fornito all'aria da HVAC ad aria
Note on G56: Luca Caruso: calore ceduto per convezione da HVAC non tutt'aria (radiatori, travi fredde ecc)
Note on I71: Luca Caruso: sum of all the capacitive elements of the envelope.